Procedure

Functional Safety

[Enter Project Name]

| Document Number | Revision | Date |
| --- | --- | --- |
| RTPR-HSE-PRO-XXXX | Rev 0 | 30/06/2026 |

| Status | Name | Position | Signature |
| --- | --- | --- | --- |
| Originator | Ashleigh Phillips | [External] HSES Industry Partners |  |
| Reviewed | Kirsten Snyman | Snr Manager, CSP RioProjects |  |
| Reviewed | Matt Moroz | Snr Manager, HSES RioProjects |  |
| Approved | Greg Doyle | Vice President HSESC, SD&T |  |

Contents

0	How to Use This Document	3

0.1	Purpose of This Template	3

0.2	How This Document is Structured	3

0.3	Step-by-Step Completion Instructions	3

0.4	Pre-Issue Checklist	4

0.5	Document Relationships	4

1	Heading	6

Heading

INSTRUCTION: Read, action and delete this box before this procedure is issued. Delete the entire Section 0 before this document is submitted for review or approval. It must not appear in any approved version of this procedure.

0  How to Use This Document

This section explains the purpose of the template, how it is structured, the sequence for completing it and the checks required before it is issued. It must be read in full before any section of this document is completed. Delete Section 0 in its entirety before issue.

0.1  Purpose of This Template

This template supports the preparation of a project-specific Functional Safety Procedure for projects delivered under an Owner-Led model. Under this model, Rio Tinto directly manages all project activities, and this procedure applies to all personnel on the project, including Rio Tinto staff and all contractor organisations.

This template is provided as a 90% draft. Fixed content reflects the minimum Rio Tinto requirement and must not be reduced. The remaining 10% covers role names, register locations, schedules and project-specific triggers, and must be completed by the project team before issue.

0.2  How This Document is Structured

This document contains four content types:

Fixed content is plain black text reflecting minimum Rio Tinto requirements. Fixed content must not be reduced, deleted or overridden.

[INSERT: placeholder text] appears in blue bold. Each placeholder must be replaced with accurate, project-specific information before issue.

Orange text marks specific who, what, when, or how detail included as a best practice suggestion. The project team may retain, modify, or replace orange detail.

0.3  Pre-Issue Checklist

Before submitting this document for review or approval, confirm all items below are complete, then delete this checklist together with the rest of Section 0.

| Check | Complete? |
| --- | --- |
| Cover page is complete including document number, revision, date and signatories | ☐ |
| All [INSERT:] placeholder text has been replaced with project-specific information | ☐ |
| All instruction boxes have been read, actioned and deleted | ☐ |
| All role titles match the actual project organisational structure | ☐ |
| All system and register locations are confirmed and inserted | ☐ |
| All workshop and meeting dates are confirmed against the project programme | ☐ |
| Related procedures in the References section are issued or being issued concurrently | ☐ |
| Section 17 (Source Requirements Traceability) will be deleted before final issue | ☐ |
| Section 16 (Project Localisation Edits) has been populated with all changes made during preparation | ☐ |
| Section 0 has been deleted in its entirety | ☐ |

1  Purpose and Scope

This section defines the purpose of this procedure, the project lifecycle phases within scope, and the obligations it establishes from project Execution through to Handover.

1.1  Purpose of This Document

This section states the purpose of this procedure and the requirements it establishes for the project.

This procedure defines requirements for managing Safety Instrumented Systems (SIS) and other functional safety systems to ensure they remain capable of performing their intended safety function throughout their lifecycle — from design through commissioning, operation, maintenance, modification, and decommissioning.

1.2  Scope of This Document

This section defines which activities and lifecycle phases are governed by this document.

This procedure applies to all Rio Tinto project personnel and all contractor organisations performing work under an Owner-Led project. It governs functional safety from project Execution through to Handover.

[INSERT: scope qualifications] — note any activities, phases, or locations excluded from this procedure's scope

2  Roles and Responsibilities

This section defines the responsibilities for all project roles relevant to this procedure, covering the Rio Tinto project team and all contractor organisations. Responsibilities are aligned to governance, oversight, assessment execution, reporting, and control verification.

| Responsibilities | Company | Contractor | Section |
| --- | --- | --- | --- |
| Project Management |  |  |  |
| Holds overall accountability for project compliance with this procedure and approves this procedure and any material amendment. | ✓ |  |  |
| Accepts residual risk at the highest risk class level and authorises continuation where escalation is required. | ✓ |  |  |
| [INSERT: add further responsibilities as required] |  |  |  |
| HSE/CSP Management |  |  |  |
| Maintains and implements this procedure and confirms all activities meet its requirements before work proceeds. | ✓ | ✓ |  |
| Reviews and approves all required assessments, plans, and registers produced under this procedure. | ✓ | ✓ |  |
| Reports performance against this procedure at the agreed project HSESC performance meeting. | ✓ | ✓ |  |
| Reviews performance data, identifies trends, and incorporates systemic findings into corrective action programmes. | ✓ | ✓ |  |
| [INSERT: add further responsibilities as required] |  |  |  |
| Frontline Supervision |  |  |  |
| Ensures work crew compliance with this procedure before and during all relevant task executions. | ✓ | ✓ |  |
| Stops work when the requirements of this procedure cannot be met and notifies the HSESC Manager. | ✓ | ✓ |  |
| Confirms all personnel under their supervision are trained and competent before commencing relevant activities. | ✓ | ✓ |  |
| [INSERT: add further responsibilities as required] |  |  |  |
| All Project Personnel / Workers |  |  |  |
| Complies with the requirements of this procedure in all relevant work activities. | ✓ | ✓ |  |
| Reports any non-compliance with this procedure immediately to their supervisor. | ✓ | ✓ |  |
| [INSERT: add further responsibilities as required] |  |  |  |

3  Safety Requirements and SIL Classification

This section defines the functional safety lifecycle requirements, the SIL determination methodology approved for this project, and the documentation standards that apply from concept through decommissioning.

3.1  Functional Safety Lifecycle Requirements

The functional safety lifecycle governs all safety instrumented functions from concept through decommissioning on this project.

The RT Process Safety Standard and RT Functional Safety Standard require that functional safety lifecycle requirements are defined and applied from concept through decommissioning. The Project Manager confirms that a functional safety lifecycle plan is in place before detailed design commences, covering each phase from concept, design, installation, commissioning, operation, and decommissioning.

The IFC EHS General Guidelines §2.8 require that safety instrumented systems and safety instrumented functions are designed by competent personnel and that the design basis is documented and retained for the life of the system. The Functional Safety Engineer confirms that design basis documentation is placed under document control and retained in the project document management system.

The Functional Safety Engineer confirms competency requirements for personnel responsible for functional safety design activities are met before those activities commence. Functional safety competency requirements for this project are defined in Section 4 of this procedure. Training and competency records are managed under the Training Procedure, refer RTPR-HSE-PRO-0004.

3.2  SIL Determination Methodology

SIL determination applies to all safety functions on this project and must be completed before the Safety Requirements Specification is prepared.

The RT Process Safety Standard and RT Functional Safety Standard require that a Safety Integrity Level is determined for every safety instrumented function based on a documented risk assessment. SIL determination is conducted as part of the process safety study and is not finalised without reference to the hazard and risk analysis completed under the Process Safety Procedure, refer RTPR-HSE-PRO-0019.

The project must define the methodology used for SIL determination, the authority level required to approve SIL assignments, and the process for reviewing and confirming SIL allocations at each project stage gate. The approved methodology for this project is recorded below:

[INSERT: SIL_determination_methodology] — Define the SIL determination methodology approved for this project — risk graph, Layer of Protection Analysis (LOPA), or equivalent — and insert the approved methodology or reference to the project-specific process safety study.

Table: SIL Determination Authority and Stage Gate Review

| Stage Gate | SIL Determination Activity | Responsible Role | Approval Authority |
| --- | --- | --- | --- |
| Concept | Initial SIL classification against risk criteria | Functional Safety Engineer | Process Safety Lead |
| Detailed Design Entry | Confirm SIL allocation against completed LOPA or risk graph | Functional Safety Engineer | Project Manager |
| Construction Complete | Review SIL allocations for any scope or design changes | Functional Safety Engineer | Process Safety Lead |
| [INSERT: stage gate name] | [INSERT: SIL review activity] | [INSERT: responsible role] | [INSERT: approval authority] |

3.3  Safety Requirements Specification

A Safety Requirements Specification must be prepared for each safety instrumented function before detailed design commences.

The RT Process Safety Standard and RT Functional Safety Standard require that a documented Safety Requirements Specification is prepared for each safety function before detailed design begins. The SRS records the safety function description, the SIL target, the required risk reduction, response time requirements, spurious trip tolerance, environmental conditions, and proof test interval requirements.

The Functional Safety Engineer confirms that the SRS is approved before detailed design activities commence for the relevant safety function. The SRS is placed under document control in the project document management system and is updated when a management of change process results in a change to a safety instrumented function, refer RTPR-HSE-PRO-0040.

The SRS template used for this project is defined below. All safety instrumented functions on this project must have a completed SRS before the design is finalised:

[INSERT: SRS_template_reference] — Insert the document reference and title of the approved SRS template for this project, e.g. RTPR-HSE-TMP-XXXX Safety Requirements Specification Template.

4  Design, Installation and Commissioning

This section defines the acceptance testing, commissioning documentation, and handover requirements that apply to all safety instrumented systems before they are relied upon for plant protection.

4.1  Factory Acceptance Testing and Site Acceptance Testing

FAT and SAT are mandatory for all safety instrumented systems on this project and must be completed before commissioning.

The RT Functional Safety Standard requires that Factory Acceptance Testing and Site Acceptance Testing are completed for all safety instrumented systems before commissioning, with results documented and retained. The Functional Safety Engineer confirms that FAT and SAT procedures are prepared and approved before testing commences.

The Commissioning Manager confirms that no safety instrumented function is relied upon for plant protection until FAT and SAT have been completed, any identified deficiencies have been closed, and commissioning documentation confirming the test and verification outcome has been approved. SIS commissioning activities are governed by the Commissioning Procedure, refer RTPR-HSE-PRO-0047.

The FAT and SAT requirements for this project, including which systems require FAT, who witnesses each test, and what documentation is required, are defined in the table below:

[INSERT: FAT_SAT_requirements_table] — Define FAT and SAT requirements: which SIS require FAT; who witnesses FAT and SAT (e.g. Rio Tinto Functional Safety Engineer, Project Manager, third-party verifier); what documentation is required (test records, deficiency register, close-out sign-off). Insert as a completed table.

Table: FAT and SAT Requirements by System

| Safety Instrumented System | FAT Required | SAT Required | Witness Roles | Documentation Required | Approval Authority |
| --- | --- | --- | --- | --- | --- |
| Emergency Shutdown System (ESD) | Yes | Yes | Functional Safety Engineer, Project Manager | FAT report, SAT report, deficiency close-out register | Commissioning Manager |
| Fire and Gas Detection System | Yes | Yes | Functional Safety Engineer, Commissioning Lead | FAT report, SAT report, functional test certificate | Commissioning Manager |
| [INSERT: SIS name] | [INSERT: Yes/No] | [INSERT: Yes/No] | [INSERT: witness roles] | [INSERT: required documentation] | [INSERT: approval authority] |

4.2  SIS Handover Documentation

Handover of safety instrumented systems from the construction team to the operations team requires defined minimum documentation.

The project must define the minimum documentation requirements for SIS handover from the construction team to the operations team, ensuring that as-built documentation, test results, and proof test procedures are transferred and controlled before the system is handed over. The Commissioning Manager confirms that the handover documentation package is complete before plant protection responsibility is transferred.

The handover documentation package for each safety instrumented system must include the items listed below. The Functional Safety Engineer confirms the package is complete and the document controller confirms all items are placed under document control:

The minimum SIS handover documentation package for this project includes:

Approved as-built drawings and cause-and-effect matrices

Completed FAT and SAT reports with deficiency close-out evidence

Approved Safety Requirements Specification for each safety function

Proof test procedures for each safety function, ready for operational use

Functional safety assessment or verification report confirming SIL achievement

Maintenance and inspection schedules aligned to proof test interval requirements

[INSERT: additional_handover_documents]

Handover of SIS to operations is governed by the Commissioning Procedure, refer RTPR-HSE-PRO-0047. Any SIS that cannot be handed over with a complete documentation package is subject to a formal risk assessment and approved interim controls before the commissioning team withdraws.

5  Defeat and Bypass Management

This section defines the authorisation process, compensating controls, time limits, and reporting requirements for any defeat or bypass of a safety instrumented function.

5.1  Bypass Authorisation and Risk Assessment

No safety instrumented function may be defeated or bypassed without formal authorisation and a documented risk assessment.

The RT Process Safety Standard requires a formal authorisation process for any defeat or bypass of a safety instrumented function. The authorisation process requires a risk assessment before bypass is applied, documented compensating controls, a time-limited bypass with a defined duration, approval at the appropriate authority level, and active tracking of all active bypasses.

Any work that requires isolation or bypass of a safety instrumented system for testing or maintenance purposes is subject to the Isolation Procedure, refer RTPR-HSE-PRO-0024, and requires a permit raised via the site PTW system before commencing work, refer RTPR-HSE-PRO-0021.

The bypass authorisation requirements for this project are defined in the table below. Bypass of a safety function at a higher SIL level requires a higher approval authority level:

Table: Bypass Authorisation Requirements by SIL Level

| SIL Level | Maximum Bypass Duration | Risk Assessment Required | Compensating Controls Required | Approval Authority | Bypass Tracking Location |
| --- | --- | --- | --- | --- | --- |
| SIL 1 | 72 hours | Yes — documented JHA minimum | Yes — documented in bypass register | Operations Superintendent | Active Bypass Register |
| SIL 2 | 24 hours | Yes — formal risk assessment | Yes — documented in bypass register | Plant Manager | Active Bypass Register |
| SIL 3 | 8 hours | Yes — formal risk assessment with Functional Safety Engineer review | Yes — documented in bypass register and reported to Project Manager | Project Manager | Active Bypass Register |
| [INSERT: SIL level] | [INSERT: max duration] | [INSERT: RA type] | [INSERT: compensating controls requirement] | [INSERT: approval authority] | [INSERT: tracking location] |

5.2  Bypass Tracking and Reporting

All active bypasses of safety instrumented functions are tracked and reported as part of monthly HSESC reporting.

The APPC Appendix C §26 requirement is that bypass of any critical control is captured in the project action tracking system and reported to the project owner as part of monthly HSESC reporting. The HSESC Manager confirms that the active bypass register is reviewed at the weekly project HSESC review meeting and that any bypass approaching or exceeding its approved duration is escalated to the approval authority.

The active bypass register is maintained by the HSESC Manager and is accessible to all personnel with a role in safety instrumented system management. The register records the safety function bypassed, the reason for bypass, the compensating controls in place, the approved duration, the approval authority, and the date the bypass was closed out:

[INSERT: bypass_register_location] — Insert the document reference and storage location of the Active Bypass Register for this project, e.g. RTPR-HSE-REG-XXXX Active Bypass Register, stored in [document management system].

Any bypass that cannot be closed within the approved duration requires a new risk assessment and re-approval before the existing bypass period expires. Any safety instrumented function that has been bypassed more than twice within a 90-day period is subject to a formal review by the Functional Safety Engineer to determine whether a design or maintenance deficiency exists.

6  Testing and Maintenance

This section defines proof test interval requirements, proof test procedure standards, and the functional safety competency requirements for personnel conducting SIS testing and maintenance.

6.1  Proof Test Requirements

Proof test intervals and procedures are defined for each safety function based on its SIL target and must be followed by competent personnel.

The RT Functional Safety Standard requires that proof test interval requirements are defined based on the SIL target for each safety function, that proof test procedures are documented and followed by competent personnel, and that test results are documented and any failures investigated. The Functional Safety Engineer confirms that proof test intervals are calculated as part of the SIL verification activity and are included in the Safety Requirements Specification for each function.

Proof testing of safety instrumented functions requires a permit raised via the site PTW system before commencing work, refer RTPR-HSE-PRO-0021. Any isolation required during proof testing is conducted in accordance with the Isolation Procedure, refer RTPR-HSE-PRO-0024. Any change to a proof test procedure or interval is subject to the Management of Change Procedure, refer RTPR-HSE-PRO-0040.

The proof test procedure for each safety function must include the items listed below. The Functional Safety Engineer approves each procedure before it is used:

Each proof test procedure must document:

The safety function identifier and SIL target

The required proof test interval and the date the next test is due

The step-by-step test method, including all test equipment required

The acceptance criteria for each test step

The process for recording results and reporting any test failure or partial failure

The competency level required for the personnel conducting the test

The estimated duration of the test and the bypass period required, to support bypass authorisation planning

[INSERT: additional_proof_test_procedure_requirements]

Any failure identified during a proof test is reported as an incident and investigated in accordance with the project incident reporting requirements, refer RTPR-HSE-PRO-0009. The Functional Safety Engineer reviews the failure investigation findings to determine whether the SIL target for the affected function remains achievable with the current design and maintenance regime.

6.2  Functional Safety Competency

Personnel responsible for SIS testing and maintenance must meet defined competency requirements before undertaking those activities.

The project must define the minimum functional safety competency requirements for personnel responsible for SIS testing and maintenance, and document the process for verifying that contractors engaged in SIS work meet those requirements. Competency records are managed under the Training Procedure, refer RTPR-HSE-PRO-0004.

The functional safety competency requirements for this project are defined in the table below. The HSESC Manager confirms that competency verification is completed and recorded before any personnel are assigned to SIS testing or maintenance activities:

[INSERT: functional_safety_competency_requirements] — Define the functional safety competency requirements for this project: which roles require formal TÜV Functional Safety Engineer certification or equivalent; which roles may perform proof tests under supervision only; and what the supervision and sign-off requirements are for each category.

Table: Functional Safety Competency Requirements

| Role | Activity | Minimum Competency Requirement | Supervision Requirement | Verification Method |
| --- | --- | --- | --- | --- |
| Functional Safety Engineer | SIL determination, SRS preparation, FAT/SAT approval, proof test procedure approval | TÜV Functional Safety Engineer (FSEng) certification or equivalent recognised qualification | None — independent sign-off authority | Certificate sighted and recorded by HSESC Manager |
| SIS Technician | Proof test execution, SIS maintenance | Formal training in the specific SIS platform plus project functional safety induction | Supervised by Functional Safety Engineer for first three proof tests on this project | Training records sighted and recorded by HSESC Manager |
| Contractor SIS Technician | Proof test execution under supervision | Demonstrated competency on the specific SIS platform, verified by Functional Safety Engineer before first test | Supervised by project Functional Safety Engineer at all times | Competency assessment completed and recorded before first activity |
| [INSERT: role] | [INSERT: activity] | [INSERT: minimum competency] | [INSERT: supervision requirement] | [INSERT: verification method] |

The HSESC Manager confirms that the competency requirements table above is reviewed at each major project phase gate and updated when scope changes result in new SIS activities or new contractor organisations being engaged in SIS work.

7  Definitions and Acronyms

The following terms are used throughout this procedure. Where a term is also used in other project HSESC procedures, the definition below applies consistently across the system.

| Term | Definition |
| --- | --- |
| SIL | Safety Integrity Level — a discrete level (1 to 4) for specifying the safety integrity requirements of safety instrumented functions to be allocated to safety instrumented systems, as defined in IEC 61511. |
| SIS | Safety Instrumented System — an instrumented system used to implement one or more safety instrumented functions, composed of any combination of sensors, logic solvers, and final elements. |
| SIF | Safety Instrumented Function — a safety function with a specified safety integrity level that is implemented by a safety instrumented system and is intended to achieve or maintain a safe state of the process with respect to a specific hazardous event. |
| SRS | Safety Requirements Specification — a document that specifies the requirements for a safety instrumented system, including the required safety integrity level, process conditions, and functional requirements for each safety instrumented function. |
| LOPA | Layer of Protection Analysis — a semi-quantitative risk assessment method used to determine whether sufficient independent layers of protection exist to reduce risk to a tolerable level, and to establish SIL targets for safety instrumented functions. |
| PFD | Probability of Failure on Demand — a measure of the likelihood that a safety instrumented function will fail to respond correctly when a demand is placed upon it, used to verify that a required SIL is achieved. |
| PFDavg | Average Probability of Failure on Demand — the average value of the probability of failure on demand over a proof test interval, used as the primary metric for SIL verification in low demand mode of operation. |
| HAZOP | Hazard and Operability Study — a structured and systematic examination of a planned or existing process or operation in order to identify and evaluate problems that may represent risks to personnel or equipment. |
| IPL | Independent Protection Layer — a device, system, or action that is capable of preventing a scenario from proceeding to an undesired consequence, independent of the initiating event or the action of any other protection layer. |
| FAT | Factory Acceptance Test — a testing phase conducted at the manufacturer's facility to verify that a safety instrumented system or component meets specified design and functional requirements prior to delivery to site. |
| SAT | Site Acceptance Test — a testing phase conducted at the installation site to verify that a safety instrumented system has been correctly installed, configured, and functions in accordance with the safety requirements specification. |
| PTW | Permit to Work — a formal documented system used to control non-routine work activities, including the testing and maintenance of safety instrumented systems, as governed by RTPR-HSE-PRO-0021. |
| MoC | Management of Change — a systematic process for reviewing, approving, and documenting proposed changes to equipment, processes, procedures, or organisational structures that may affect safety, as governed by RTPR-HSE-PRO-0040. |
| BPCS | Basic Process Control System — a system that responds to input signals from the process and its associated equipment and generates output signals causing the process and its associated equipment to operate in the desired manner. |
| ESD | Emergency Shutdown — a safety instrumented function or system designed to bring a process to a safe state upon detection of a hazardous condition, typically implemented as a discrete SIF within a SIS. |
| HIPPS | High Integrity Pressure Protection System — a type of safety instrumented system designed to prevent overpressure of a vessel or pipeline by isolating the pressure source, replacing or supplementing traditional pressure relief devices. |
| FSE | Functional Safety Engineer — a competent person responsible for the engineering, assessment, and verification of safety instrumented systems and safety instrumented functions in accordance with IEC 61511 and project requirements. |
| FSA | Functional Safety Assessment — a structured investigation to judge the functional safety achieved by one or more protective systems, conducted at defined phases of the safety lifecycle to confirm compliance with requirements. |
| MTTR | Mean Time To Repair — the average time required to restore a failed safety instrumented system component to an operational state, used in reliability and availability calculations for SIL verification. |
| MTTF | Mean Time To Failure — the average time a safety instrumented system component operates before failing, used in quantitative reliability assessments to verify that SIL targets are achieved. |
| DC | Diagnostic Coverage — the percentage of dangerous failures of a component or subsystem that are detected by automatic diagnostic tests, used in safety integrity level verification calculations. |
| CCF | Common Cause Failure — a failure in which multiple components fail due to the same root cause, which can undermine the independence and redundancy assumed in safety instrumented system designs. |
| TI | Test Interval — the maximum period of time between successive proof tests of a safety instrumented function, used in calculating average probability of failure on demand and verifying SIL compliance. |
| ALARP | As Low As Reasonably Practicable — a risk reduction principle requiring that residual risk be reduced to the lowest level that is reasonably practicable, balancing the cost and effort of further reduction against the benefit gained. |
| HSESC | Health, Safety, Environment, and Social, Community — the management framework under which Rio Tinto owner-led project procedures are developed and implemented to ensure integrated management of health, safety, environmental, and community risks. |
| RT | Rio Tinto — the project owner and custodian of standards, procedures, and risk management frameworks referenced throughout this procedure. |
| HSE | Health, Safety, and Environment — the discipline and associated management system governing the identification, assessment, and control of risks to people and the environment. |
| P&ID | Piping and Instrumentation Diagram — an engineering drawing that shows the piping, instrumentation, and control devices associated with a process, used as a key reference document during SIS design and verification. |
| OEM | Original Equipment Manufacturer — the manufacturer of a safety instrumented system component or subsystem, whose documentation, certificates, and data are required for SIL verification and maintenance activities. |
| IEC | International Electrotechnical Commission — the international standards body responsible for publishing IEC 61511 and IEC 61508, which form the primary functional safety framework referenced in this procedure. |
| SME | Subject Matter Expert — a person with demonstrated expertise in a specific technical discipline, such as functional safety, whose input is required during safety lifecycle activities including HAZOP, LOPA, and functional safety assessments. |
| [INSERT: add project-specific terms] | [INSERT: definition] |

8  References and Source Information

This section lists the internal and external documents this procedure relies on. This section remains in the procedure once published. Where a referenced document is updated, this procedure is reviewed to confirm the reference remains current.

| Document | Reference | Type |
| --- | --- | --- |
| Rio Tinto Risk Management Standard | RT Risk Management Standard | External RT |
| Rio Tinto Risk Management Standard — Appendix C, Requirement C-1 | RT Risk Management Standard Appendix C C-1 | External RT |
| Process Safety Procedure | RTPR-HSE-PRO-0019 | Internal procedure |
| Permit to Work Procedure | RTPR-HSE-PRO-0021 | Internal procedure |
| Isolation Procedure | RTPR-HSE-PRO-0024 | Internal procedure |
| Management of Change Procedure | RTPR-HSE-PRO-0040 | Internal procedure |
| Commissioning Procedure | RTPR-HSE-PRO-0047 | Internal procedure |
| Training Procedure | RTPR-HSE-PRO-0004 | Internal procedure |
| Functional Safety of Safety Instrumented Systems for the Process Industry Sector — Part 1: Framework, Definitions, System, Hardware and Application Programming Requirements | IEC 61511-1:2016 | External framework |
| Functional Safety of Safety Instrumented Systems for the Process Industry Sector — Part 2: Guidelines for the Application of IEC 61511-1 | IEC 61511-2:2016 | External framework |
| Functional Safety of Safety Instrumented Systems for the Process Industry Sector — Part 3: Guidance for the Determination of the Required Safety Integrity Levels | IEC 61511-3:2016 | External framework |
| Functional Safety of Electrical/Electronic/Programmable Electronic Safety-Related Systems | IEC 61508:2010 | External framework |
| Layer of Protection Analysis — Simplified Process Risk Assessment | CCPS LOPA Guideline | External framework |
| [INSERT: further referenced document, where applicable] | [INSERT: reference] | [INSERT: type] |

9  Project Localisation Edits

This section captures the project-specific edits made to this document during preparation. This section stays in the document once published and is updated at each document revision. Record all additions, deletions, and wording changes from the original template.

Records of wording changes

| Description of the Change | Section |
| --- | --- |
| [INSERT: description of change] | [INSERT: section] |
| [INSERT: description of change] | [INSERT: section] |
| [INSERT: description of change] | [INSERT: section] |

Records of new content additions

| Description of the Change | Section |
| --- | --- |
| [INSERT: description of change] | [INSERT: section] |
| [INSERT: description of change] | [INSERT: section] |
| [INSERT: description of change] | [INSERT: section] |

Records of content removal

| Description of the Change | Section |
| --- | --- |
| [INSERT: description of change] | [INSERT: section] |
| [INSERT: description of change] | [INSERT: section] |
| [INSERT: description of change] | [INSERT: section] |

REMOVABLE SECTION — Source Requirements Traceability. Delete this entire section before the document is issued for approval. It must not appear in any approved version of this document. Table A records requirements addressed in this procedure. Table B records requirements not fully addressed, with written justification for each.

10  Source Requirements Traceability (DELETE BEFORE ISSUE)

10.1  Requirements Addressed in This Procedure

| Section | Source | Requirement | Status |
| --- | --- | --- | --- |
| [INSERT: section] | RT Standard Process Safety Standard and Functional Safety Standard | Requires functional safety lifecycle management from concept through decommissioning, including SIL determination, Safety Requirements Specifications, FAT/SAT, bypass management, and proof test intervals for all SIS. | Full |
| [INSERT: section] | IFC EHS General Guidelines §2.8 | Requires that SIS and safety instrumented functions are designed by competent personnel with documented design basis retained for the life of the system, and that adequate ventilation and confined space management practices are maintained. | Full |
| [INSERT: section] | Appendix C C-1 §26 | Requires that any bypass of a critical control is captured in the project action tracking system and reported to the project owner as part of monthly HSESC reporting. | Full |

10.2  Requirements Not Fully Addressed in This Procedure

List any requirements from the external sources above that are not fully addressed in this document, with a specific written justification for each. Acceptable justifications: (a) the requirement is owned by a named standalone procedure cross-referenced here; (b) excluded by a specific business decision endorsed by project leadership, named here; or (c) addressed through an operational control outside this document, identified here.

| Requirement Not Covered | Source | Justification |
| --- | --- | --- |
| [INSERT: description of requirement not covered] | [INSERT: source and clause] | [INSERT: specific written justification] |